## PGD
Technical lists
Reference :
[6 empty] | Cust. N° : | -
|  |  | Institute for basic science |  |  | Project n° :
Page :
신동 SRF 시험시설동 액화기의 EPICS PV 정리
EPICS PV list for L280
WARNING :
|  | Date : |  |  | Distribution :
2019-04-15
|  | Author : |  | Checking : | Approval :
|  | Sungwon YOON |  | - | -
|  | Visa : |  | Visa : | Visa :
Technical lists
Reference :
[6 empty] | Cust. N° | -
|  |  | Institute for basic science |  |  | Project n° :
Page :
EPICS PV list for L280
MODIFICATIONS RECORDS
This document replaces the following document(s) :
Data Exchange list_V00.xlsx
| Revision | Date | Comments |  | Author | Checked | Approved
| 0 | 2019-04-15 | For test between PLC and EPICS IOC |  | SY
| 0.1 | 2019-04-22 | Modify some PVs (Red) |  | SY

## EPICS PVs
*실제 필드 시그널이 아닌 EPICS IOC 가상의 PV에 대한 구성 내용을 정의 한다.
Virtual PVs
Full RAON Naming (PVName) | Description | Siemans PLC | [7 empty] | EPICS IOC
|  | PLC tag name | DB address | [6 empty] | Type | Input PVs | Output PVs | Engineering Unit | Unit Conversion | Calc. Expression | Init. Value | Precision | Scan (Monitor/Scan) | Archiving | Archiving Rate | Alarm (Analog, Digital) |  |  |  |  | Alarm Severity (Analog, Digital) |  |  |  |  | High Limit | Low Limit | Read Only | Other System
|  |  | Data type | DB address | Byte | Word |  | Connect | Bit offset | (AI,AO,BI,BO,Calc,…) |  |  |  | (Y)es/(N)o |  |  |  | Event/(.1,.2,.5,1,2,5,10) | (Y)es/(N)o | (E)vent/(.1 ~ 86400) | HiHi | High | Low | LoLo | (O)pen/(C)lose | HiHi(Major) | High(Minor) | Low(Minor) | LoLo(Major) | (O)pen/(C)lose |  |  | (Y)es/(N)o | Input PV Name | Output PV Name
SRF01-L280:CBx01-CV3130:PercOpen | Cold box_inlet valve for turbine 1 and 2 (valve position) | UY3130_PercOut | REAL (4 bytes) | DB981 | 34 | 17 |  | 1 | - | AI | B:SCL01-CM:CM01:CA-R-T02 |  | % |  |  | 0 | 6 | 1 | Y | E | 80 | 70 | -10 | -20 |  | Major | Minor | Minor | Major |  | 100 | 0 | N
SRF01-L280:CBx01-CV3160:PercOpen | Cold box_cooldown bypass valve (valve position) | UY3160_PercOut | REAL (4 bytes) | DB981 | 46 | 23 |  | 1 | - | AI |  |  | %
SRF01-L280:CBx01-CV3170:PercOpen | Cold box_JT valve to dewar (valve position) | UY3170_PercOut | REAL (4 bytes) | DB981 | 50 | 25 |  | 1 | - | AI |  |  | %
SRF01-L280:CBx01-CV3290:PercOpen | Cold box_return valve from dewar (valve position) | UY3290_PercOut | REAL (4 bytes) | DB981 | 54 | 27 |  | 1 | - | AI |  |  | %
SRF01-L280:WCS01-CV2250:PercOpen | Gas management_bypass valve (valve position) | UY2250_PercOut | REAL (4 bytes) | DB981 | 146 | 73 |  | 1 | - | AI |  |  | %
SRF01-L280:WCS01-CV2160:PercOpen | Gas management_load valve (valve position) | UY2160_PercOut | REAL (4 bytes) | DB981 | 150 | 75 |  | 1 | - | AI |  |  | %
SRF01-L280:WCS01-CV2150:PercOpen | Gas management_unload valve (valve position) | UY2150_PercOut | REAL (4 bytes) | DB981 | 154 | 77 |  | 1 | - | AI |  |  | %
SRF01-L280:CBx01-AS3001:Warn | General_flashlight caution | UAH1010_Output | BOOL (1 bit) | DB981 | 162 | 81 |  |  | 0 | DI |  |  | -
SRF01-L280:CBx01-AS3002:Error | General_flashlight fault | UAHH1011_Output | BOOL (1 bit) | DB981 | 162 | 81 |  |  | 1 | DI |  |  | -
SRF01-L280:CBx01-XV3410:StateOpen | Cold box_internal purifier regeneration 1 valve (open/close state) | US3410_Output | BOOL (1 bit) | DB981 | 165 | 82 |  |  | 0 | DI |  |  | -
SRF01-L280:CBx01-XV3415:StateOpen | Cold box_internal purifier LIN blow off valve (open/close state) | US3415_Output | BOOL (1 bit) | DB981 | 165 | 82 |  |  | 1 | DI |  |  | -
SRF01-L280:CBx01-PT3905:Press | Cold box_insulation vacuum value | PI3905_Value | REAL (4 bytes) | DB981 | 180 | 90 |  | 1 | - | AI |  |  | mbar
SRF01-L280:CBx01-PT3905:State | Cold box_insulation vacuum state | PI3905_Sta | WORD (2 bytes) | DB981 | 184 | 92 |  | 1 | - | AI |  |  | -
SRF01-L280:CBx01-TT3112:State | Cold box_E3110 outlet temperature state | TI3112_Sta | WORD (2 bytes) | DB981 | 196 | 98 |  | 1 | - | AI |  |  | -
SRF01-L280:CBx01-TT3130:State | Cold box_turbine 1 inlet temperature state | TI3130_Sta | WORD (2 bytes) | DB981 | 202 | 101 |  | 1 | - | AI |  |  | -
SRF01-L280:CBx01-TT3155:State | Cold box_turbine 2 outlet temperature state | TI3155_Sta | WORD (2 bytes) | DB981 | 208 | 104 |  | 1 | - | AI |  |  | -
SRF01-L280:CBx01-TT3280:State | Cold box_turbine 2 outlet temperature state from dewar | TI3280_Sta | WORD (2 bytes) | DB981 | 214 | 107 |  | 1 | - | AI |  |  | -
SRF01-L280:CBx01-TT3501A:TempK | Cold box_adsorber A inlet temperature value | TI3501A_Value | REAL (4 bytes) | DB981 | 264 | 132 | 0 | 2/1 | - | AI |  |  | K
SRF01-L280:CBx01-TT3501A:State | Cold box_adsorber A inlet temperature state | TI3501A_Sta | WORD (2 bytes) | DB981 | 268 | 134 | 2 | 2/1 | - | AI |  |  | -
SRF01-L280:CBx01-TT3501B:TempK | Cold box_adsorber B inlet temperature value | TI3501B_Value | REAL (4 bytes) | DB981 | 270 | 135 | 3 | 2/1 | - | AI |  |  | K
SRF01-L280:CBx01-TT3501B:State | Cold box_adsorber B inlet temperature state | TI3501B_Sta | WORD (2 bytes) | DB981 | 274 | 137 | 5 | 2/1 | - | AI |  |  | -
SRF01-L280:CBx01-PT3130:Press | Cold box_turbine 1 inlet pressure value | PI3130_Value | REAL (4 bytes) | DB981 | 288 | 144 | 12 | 2/1 | - | AI |  |  | bara
SRF01-L280:CBx01-PT3130:State | Cold box_turbine 1 inlet pressure state | PI3130_Sta | WORD (2 bytes) | DB981 | 292 | 146 | 14 | 2/1 | - | AI |  |  | -
SRF01-L280:CBx01-ST3131:Speed | Cold box_turbine 1 rotating speed value | SI3131_Value | REAL (4 bytes) | DB981 | 294 | 147 | 15 | 2/1 | - | AI |  |  | RPS
SRF01-L280:CBx01-ST3131:State | Cold box_turbine 1 rotating speed state | SI3131_Sta | WORD (2 bytes) | DB981 | 298 | 149 | 17 | 2/1 | - | AI |  |  | -
SRF01-L280:CBx01-PT3150:Press | Cold box_turbine 2 inlet pressure value | PI3150_Value | REAL (4 bytes) | DB981 | 300 | 150 | 18 | 2/1 | - | AI |  |  | bara
SRF01-L280:CBx01-PT3150:State | Cold box_turbine 2 inlet pressure state | PI3150_Sta | WORD (2 bytes) | DB981 | 304 | 152 | 20 | 2/1 | - | AI |  |  | -
SRF01-L280:CBx01-ST3151:Speed | Cold box_turbine 2 rotating speed value | SI3151_Value | REAL (4 bytes) | DB981 | 306 | 153 | 21 | 2/1 | - | AI |  |  | RPS
SRF01-L280:CBx01-ST3151:State | Cold box_turbine 2 rotating speed state | SI3151_Sta | WORD (2 bytes) | DB981 | 310 | 155 | 23 | 2/1 | - | AI |  |  | -
SRF01-L280:CBx01-PT3290:Press | Cold box_cold gas return pressure value from dewar | PI3290_Value | REAL (4 bytes) | DB981 | 312 | 156 | 24 | 2/1 | - | AI |  |  | bara
SRF01-L280:CBx01-PT3290:State | Cold box_cold gas return pressure state from dewar | PI3290_Sta | WORD (2 bytes) | DB981 | 316 | 158 | 26 | 2/1 | - | AI |  |  | -
SRF01-L280:Dwr01-LT5200:level | Dewar_LHe level percent in dewar | LI5200_Value | REAL (4 bytes) | DB981 | 324 | 162 | 30 | 2/1 | - | AI |  |  | %
SRF01-L280:Dwr01-LT5200:State | Cold box_LHe level state in dewar | LI5200_Sta | WORD (2 bytes) | DB981 | 328 | 164 | 32 | 2/1 | - | AI |  |  | -
SRF01-L280:WCS01-PT2160:Press | Gas management_high pressure value | PI2160_Value | REAL (4 bytes) | DB981 | 420 | 210 | 0 | 2/2 | - | AI |  |  | bara
SRF01-L280:WCS01-PT2160:State | Gas management_high pressure state | PI2160_Sta | WORD (2 bytes) | DB981 | 424 | 212 | 2 | 2/2 | - | AI |  |  | -
SRF01-L280:WCS01-PT2170:Press | Gas management_buffer tank pressure value | PI2170_Value | REAL (4 bytes) | DB981 | 426 | 213 | 3 | 2/2 | - | AI |  |  | bara
SRF01-L280:WCS01-PT2170:State | Gas management_buffer tank pressure state | PI2170_Sta | WORD (2 bytes) | DB981 | 430 | 215 | 5 | 2/2 | - | AI |  |  | -
SRF01-L280:WCS01-PT2240:Press | Gas management_low pressure value | PI2240_Value | REAL (4 bytes) | DB981 | 432 | 216 | 6 | 2/2 | - | AI |  |  | bara
SRF01-L280:WCS01-PT2240:State | Gas management_low pressure state | PI2240_Sta | WORD (2 bytes) | DB981 | 436 | 218 | 8 | 2/2 | - | AI |  |  | -
SRF01-L280:CBx01-TT3112:TempK | Cold box_E3110 outlet temperature value | TI3112_K | REAL (4 bytes) | DB981 | 500 | 250 | 40 | 2/3 | - | AI |  |  | K
SRF01-L280:CBx01-TT3130:TempK | Cold box_turbine 1 inlet temperature value | TI3130_Value | REAL (4 bytes) | DB981 | 506 | 253 | 43 | 2/3 | - | AI |  |  | K
SRF01-L280:CBx01-TT3155:TempK | Cold box_turbine 2 outlet temperature value | TI3155_Value | REAL (4 bytes) | DB981 | 512 | 256 | 46 | 2/3 | - | AI |  |  | K
SRF01-L280:CBx01-TT3280:TempK | Cold box_cold gas return temperature value from dewar | TI3280_Value | REAL (4 bytes) | DB981 | 518 | 259 | 49 | 2/3 | - | AI |  |  | K
SRF01-L280:CBx01-CV3130:ManRmp | Cold box_inlet valve for turbine 1 and 2 (Ramp up manual value) | UY3130_RmpMan | REAL (4 bytes) | DB982 | 34 | 17 |  | 3/1 | - | AO |  |  | %
SRF01-L280:CBx01-CV3160:ManRmp | Cold box_cooldown bypass valve (Ramp up manual value) | UY3160_RmpMan | REAL (4 bytes) | DB982 | 46 | 23 |  | 3/1 | - | AO |  |  | %
SRF01-L280:CBx01-CV3170:ManRmp | Cold box_JT valve (Ramp up manual value) | UY3170_RmpMan | REAL (4 bytes) | DB982 | 50 | 25 |  | 3/1 | - | AO |  |  | %
SRF01-L280:CBx01-CV3290:ManRmp | Cold box_return valve from dewar (Ramp up manual value) | UY3290_RmpMan | REAL (4 bytes) | DB982 | 54 | 27 |  | 3/1 | - | AO |  |  | %
SRF01-L280:WCS01-CV2250:ManRmp | Gas management_bypass valve (Ramp up manual value) | UY2250_RmpMan | REAL (4 bytes) | DB982 | 146 | 73 |  | 3/2 | - | AO |  |  | %
SRF01-L280:WCS01-CV2160:ManRmp | Gas management_load valve (Ramp up manual value) | UY2160_RmpMan | REAL (4 bytes) | DB982 | 150 | 75 |  | 3/2 | - | AO |  |  | %
SRF01-L280:WCS01-CV2150:ManRmp | Gas management_unload valve (Ramp up manual value) | UY2150_RmpMan | REAL (4 bytes) | DB982 | 154 | 77 |  | 3/2 | - | AO |  |  | %
SRF01-L280:CBx01-CV3130:ManVal | Cold box_inlet valve for turbine 1 and 2 (%open manual value) | UY3130_ManVal | REAL (4 bytes) | DB982 | 186 | 93 |  | 3/2 | - | AO |  |  | %
SRF01-L280:CBx01-CV3160:ManVal | Cold box_cooldown bypass valve (%open manual value) | UY3160_ManVal | REAL (4 bytes) | DB982 | 198 | 99 |  | 3/2 | - | AO |  |  | %
SRF01-L280:CBx01-CV3170:ManVal | Cold box_JT valve (%open manual value) | UY3170_ManVal | REAL (4 bytes) | DB982 | 202 | 101 |  | 3/2 | - | AO |  |  | %
SRF01-L280:CBx01-CV3290:ManVal | Cold box_return valve from dewar (%open manual value) | UY3290_ManVal | REAL (4 bytes) | DB982 | 206 | 103 |  | 3/2 | - | AO |  |  | %
SRF01-L280:WCS01-CV2250:ManVal | Gas management_bypass valve (%open manual value) | UY2250_ManVal | REAL (4 bytes) | DB982 | 298 | 149 |  | 3/2 | - | AO |  |  | %
SRF01-L280:WCS01-CV2160:ManVal | Gas management_load valve (%open manual value) | UY2160_ManVal | REAL (4 bytes) | DB982 | 302 | 151 |  | 3/2 | - | AO |  |  | %
SRF01-L280:WCS01-CV2150:ManVal | Gas management_unload valve (%open manual value) | UY2150_ManVal | REAL (4 bytes) | DB982 | 306 | 153 |  | 3/2 | - | AO |  |  | %
SRF01-L280:CBx01-CV3130:Man | Cold box_Inlet valve for turbine 1 and 2 (1: manual mode) | UY3130_Man | BOOL (1 bit) | DB982 | 314 | 157 |  |  | 6 | DO |  |  | -
SRF01-L280:CBx01-CV3160:Man | Cold box_cooldown bypass valve (1: manual mode) | UY3160_Man | BOOL (1 bit) | DB982 | 315 | 158 |  |  | 1 | DO |  |  | -
SRF01-L280:CBx01-CV3170:Man | Cold box_JT valve (1: manual mode) | UY3170_Man | BOOL (1 bit) | DB982 | 315 | 158 |  |  | 2 | DO |  |  | -
SRF01-L280:CBx01-CV3290:Man | Cold box_return valve from dewar (1: manual mode) | UY3290_Man | BOOL (1 bit) | DB982 | 315 | 158 |  |  | 3 | DO |  |  | -
SRF01-L280:WCS01-CV2250:Man | Gas management_bypass valve (1: manual mode) | UY2250_Man | BOOL (1 bit) | DB982 | 318 | 159 |  |  | 2 | DO |  |  | -
SRF01-L280:WCS01-CV2160:Man | Gas management_load valve (1: manual mode) | UY2160_Man | BOOL (1 bit) | DB982 | 318 | 159 |  |  | 3 | DO |  |  | -
SRF01-L280:WCS01-CV2150:Man | Gas management_unload valve (1: manual mode) | UY2150_Man | BOOL (1 bit) | DB982 | 318 | 159 |  |  | 4 | DO |  |  | -
SRF01-L280:CBx01-XV3410:Man | Cold box_internal purifier regeneration 1 valve (1: manual mode) | US3410_ManMode | BOOL (1 bit) | DB982 | 326 | 163 |  |  | 0 | DO |  |  | -
SRF01-L280:CBx01-XV3410:ManOpen | Cold box_internal purifier regeneration 1 valve (1: open) | US3410_OnOffMan | BOOL (1 bit) | DB982 | 326 | 163 |  |  | 1 | DO |  |  | -
SRF01-L280:CBx01-XV3415:Man | Cold box_internal purifier LIN blow off valve (1: manual mode) | US3415_ManMode | BOOL (1 bit) | DB982 | 326 | 163 |  |  | 2 | DO |  |  | -
SRF01-L280:CBx01-XV3415:ManOpen | Cold box_internal purifier LIN blow off valve (1: open) | US3415_OnOffMan | BOOL (1 bit) | DB982 | 326 | 163 |  |  | 3 | DO |  |  | -
SRF01-L280:CBx01-CV3130:ManRmpRB | Cold box_inlet valve for turbine 1 and 2 (Ramp up manual value) | UY3130_RmpMan | REAL (4 bytes) | DB983 | 34 | 17 |  | 4/1 | - | AI |  |  | %
SRF01-L280:CBx01-CV3160:ManRmpRB | Cold box_cooldown bypass valve (Ramp up manual value) | UY3160_RmpMan | REAL (4 bytes) | DB983 | 46 | 23 |  | 4/1 | - | AI |  |  | %
SRF01-L280:CBx01-CV3170:ManRmpRB | Cold box_JT valve (Ramp up manual value) | UY3170_RmpMan | REAL (4 bytes) | DB983 | 50 | 25 |  | 4/1 | - | AI |  |  | %
SRF01-L280:CBx01-CV3290:ManRmpRB | Cold box_return valve from dewar (Ramp up manual value) | UY3290_RmpMan | REAL (4 bytes) | DB983 | 54 | 27 |  | 4/1 | - | AI |  |  | %
SRF01-L280:WCS01-CV2250:ManRmpRB | Gas management_bypass valve (Ramp up manual value) | UY2250_RmpMan | REAL (4 bytes) | DB983 | 146 | 73 |  | 4/2 | - | AI |  |  | %
SRF01-L280:WCS01-CV2160:ManRmpRB | Gas management_load valve (Ramp up manual value) | UY2160_RmpMan | REAL (4 bytes) | DB983 | 150 | 75 |  | 4/2 | - | AI |  |  | %
SRF01-L280:WCS01-CV2150:ManRmpRB | Gas management_unload valve (Ramp up manual value) | UY2150_RmpMan | REAL (4 bytes) | DB983 | 154 | 77 |  | 4/2 | - | AI |  |  | %
SRF01-L280:CBx01-CV3130:ManValRB | Cold box_inlet valve for turbine 1 and 2 (%open manual value) | UY3130_ManVal | REAL (4 bytes) | DB983 | 186 | 93 |  | 4/2 | - | AI |  |  | %
SRF01-L280:CBx01-CV3160:ManValRB | Cold box_cooldown bypass valve (%open manual value) | UY3160_ManVal | REAL (4 bytes) | DB983 | 198 | 99 |  | 4/2 | - | AI |  |  | %
SRF01-L280:CBx01-CV3170:ManValRB | Cold box_JT valve (%open manual value) | UY3170_ManVal | REAL (4 bytes) | DB983 | 202 | 101 |  | 4/2 | - | AI |  |  | %
SRF01-L280:CBx01-CV3290:ManValRB | Cold box_return valve from dewar (%open manual value) | UY3290_ManVal | REAL (4 bytes) | DB983 | 206 | 103 |  | 4/2 | - | AI |  |  | %
SRF01-L280:WCS01-CV2250:ManValRB | Gas management_bypass valve (%open manual value) | UY2250_ManVal | REAL (4 bytes) | DB983 | 298 | 149 |  | 4/2 | - | AI |  |  | %
SRF01-L280:WCS01-CV2160:ManValRB | Gas management_load valve (%open manual value) | UY2160_ManVal | REAL (4 bytes) | DB983 | 302 | 151 |  | 4/2 | - | AI |  |  | %
SRF01-L280:WCS01-CV2150:ManValRB | Gas management_unload valve (%open manual value) | UY2150_ManVal | REAL (4 bytes) | DB983 | 306 | 153 |  | 4/2 | - | AI |  |  | %
SRF01-L280:CBx01-CV3130:ManRB | Cold box_Inlet valve for turbine 1 and 2 (1: manual mode) | UY3130_Man | BOOL (1 bit) | DB983 | 314 | 157 |  |  | 6 | DI |  |  | -
SRF01-L280:CBx01-CV3160:ManRB | Cold box_cooldown bypass valve (1: manual mode) | UY3160_Man | BOOL (1 bit) | DB983 | 315 | 158 |  |  | 1 | DI |  |  | -
SRF01-L280:CBx01-CV3170:ManRB | Cold box_JT valve (1: manual mode) | UY3170_Man | BOOL (1 bit) | DB983 | 315 | 158 |  |  | 2 | DI |  |  | -
SRF01-L280:CBx01-CV3290:ManRB | Cold box_return valve from dewar (1: manual mode) | UY3290_Man | BOOL (1 bit) | DB983 | 315 | 158 |  |  | 3 | DI |  |  | -
SRF01-L280:WCS01-CV2250:ManRB | Gas management_bypass valve (1: manual mode) | UY2250_Man | BOOL (1 bit) | DB983 | 318 | 159 |  |  | 2 | DI |  |  | -
SRF01-L280:WCS01-CV2160:ManRB | Gas management_load valve (1: manual mode) | UY2160_Man | BOOL (1 bit) | DB983 | 318 | 159 |  |  | 3 | DI |  |  | -
SRF01-L280:WCS01-CV2150:ManRB | Gas management_unload valve (1: manual mode) | UY2150_Man | BOOL (1 bit) | DB983 | 318 | 159 |  |  | 4 | DI |  |  | -
SRF01-L280:CBx01-XV3410:ManRB | Cold box_internal purifier regeneration 1 valve (1: manual mode) | US3410_ManMode | BOOL (1 bit) | DB982 | 326 | 163 |  |  | 0 | DO |  |  | -
SRF01-L280:CBx01-XV3410:ManOpenRB | Cold box_internal purifier regeneration 1 valve (1: open) | US3410_OnOffMan | BOOL (1 bit) | DB982 | 326 | 163 |  |  | 1 | DO |  |  | -
SRF01-L280:CBx01-XV3415:ManRB | Cold box_internal purifier LIN blow off valve (1: manual mode) | US3415_ManMode | BOOL (1 bit) | DB982 | 326 | 163 |  |  | 2 | DO |  |  | -
SRF01-L280:CBx01-XV3415:ManOpenRB | Cold box_internal purifier LIN blow off valve (1: open) | US3415_OnOffMan | BOOL (1 bit) | DB982 | 326 | 163 |  |  | 3 | DO |  |  | -